## Field list
NOTE: Use unit-id 100 for the com.victronenergy.system data, for more information see FAQ.				ModbusTCP Register list
dbus-service-name	description	Address	Type	Scalefactor	Range	dbus-obj-path	writable	dbus-unit	Remarks
com.victronenergy.system	Serial (System)	800	string[6]	1	12 characters	/Serial	no		System value -> MAC address of CCGX (represented as string)
com.victronenergy.system	CCGX Relay 1 state	806	uint16	1	0 to 1	/Relay/0/State	yes	0=Open;1=Closed
com.victronenergy.system	CCGX Relay 2 state	807	uint16	1	0 to 1	/Relay/1/State	yes	0=Open;1=Closed	Relay 1 is available on Venus GX only.
com.victronenergy.system	PV - AC-coupled on output L1	808	uint16	1	0 to 65536	/Ac/PvOnOutput/L1/Power	no	W	Summation of all AC-Coupled PV Inverters on the output
com.victronenergy.system	PV - AC-coupled on output L2	809	uint16	1	0 to 65536	/Ac/PvOnOutput/L2/Power	no	W
com.victronenergy.system	PV - AC-coupled on output L3	810	uint16	1	0 to 65536	/Ac/PvOnOutput/L3/Power	no	W
com.victronenergy.system	PV - AC-coupled on input L1	811	uint16	1	0 to 65536	/Ac/PvOnGrid/L1/Power	no	W	Summation of all AC-Coupled PV Inverters on the input
com.victronenergy.system	PV - AC-coupled on input L2	812	uint16	1	0 to 65536	/Ac/PvOnGrid/L2/Power	no	W
com.victronenergy.system	PV - AC-coupled on input L3	813	uint16	1	0 to 65536	/Ac/PvOnGrid/L3/Power	no	W
com.victronenergy.system	PV - AC-coupled on generator L1	814	uint16	1	0 to 65536	/Ac/PvOnGenset/L1/Power	no	W	Summation of all AC-Coupled PV Inverters on a generator. Bit theoretic; this will never be used.
com.victronenergy.system	PV - AC-coupled on generator L2	815	uint16	1	0 to 65536	/Ac/PvOnGenset/L2/Power	no	W
com.victronenergy.system	PV - AC-coupled on generator L3	816	uint16	1	0 to 65536	/Ac/PvOnGenset/L3/Power	no	W
com.victronenergy.system	AC Consumption L1	817	uint16	1	0 to 65536	/Ac/Consumption/L1/Power	no	W	Power supplied by system to loads.
com.victronenergy.system	AC Consumption L2	818	uint16	1	0 to 65536	/Ac/Consumption/L2/Power	no	W
com.victronenergy.system	AC Consumption L3	819	uint16	1	0 to 65536	/Ac/Consumption/L3/Power	no	W
com.victronenergy.system	Grid L1	820	int16	1	-32768 to 32767	/Ac/Grid/L1/Power	no	W	Power supplied by Grid to system.
com.victronenergy.system	Grid L2	821	int16	1	-32768 to 32767	/Ac/Grid/L2/Power	no	W
com.victronenergy.system	Grid L3	822	int16	1	-32768 to 32767	/Ac/Grid/L3/Power	no	W
com.victronenergy.system	Genset L1	823	int16	1	-32768 to 32767	/Ac/Genset/L1/Power	no	W	Power supplied by Genset tot system.
com.victronenergy.system	Genset L2	824	int16	1	-32768 to 32767	/Ac/Genset/L2/Power	no	W
com.victronenergy.system	Genset L3	825	int16	1	-32768 to 32767	/Ac/Genset/L3/Power	no	W
com.victronenergy.system	Active input source	826	int16	1	0 to 32768	/Ac/ActiveIn/Source	no	0=Not available;1=Grid;2=Generator;3=Shore power;240=Not connected
com.victronenergy.system	Battery Voltage (System)	840	uint16	10	0 to 6553.5	/Dc/Battery/Voltage	no	V DC	Battery Voltage determined from different measurements. In order of preference: BMV-voltage (V), Multi-DC-Voltage (CV), MPPT-DC-Voltage (ScV), Charger voltage
com.victronenergy.system	Battery Current (System)	841	int16	10	-3276.8 to 3276.7	/Dc/Battery/Current	no	A DC	Postive: battery begin charged. Negative: battery being discharged
com.victronenergy.system	Battery Power (System)	842	int16	1	-32768 to 32767	/Dc/Battery/Power	no	W	Postive: battery begin charged. Negative: battery being discharged
com.victronenergy.system	Battery State of Charge (System)	843	uint16	1	0 to 100	/Dc/Battery/Soc	no	%	Best battery state of charge, determined from different measurements.
com.victronenergy.system	Battery state (System)	844	uint16	1	0 to 65536	/Dc/Battery/State	no	0=idle;1=charging;2=discharging
com.victronenergy.system	Battery Consumed Amphours (System)	845	uint16	-10	0 to -6553.6	/Dc/Battery/ConsumedAmphours	no	Ah
com.victronenergy.system	Battery Time to Go (System)	846	uint16	0,01	0 to 6553600	/Dc/Battery/TimeToGo	no	s	Special value: 0 = charging
com.victronenergy.system	PV - DC-coupled power	850	uint16	1	0 to 65536	/Dc/Pv/Power	no	W	Summation of output power of all connected Solar Chargers
com.victronenergy.system	PV - DC-coupled current	851	int16	10	-3276.8 to 3276.7	/Dc/Pv/Current	no	A DC	Summation of output current of all connected Solar Chargers
com.victronenergy.system	Charger power	855	uint16	1	0 to 65536	/Dc/Charger/Power	no	W
com.victronenergy.system	DC System Power	860	int16	1	-32768 to 32767	/Dc/System/Power	no	W	Power supplied by Battery to system.
com.victronenergy.system	VE.Bus charge current (System)	865	int16	10	-3276.8 to 3276.7	/Dc/Vebus/Current	no	A DC	Current flowing from the Multi to the dc system. Negative: the other way around.
com.victronenergy.system	VE.Bus charge power (System)	866	int16	1	-32768 to 32767	/Dc/Vebus/Power	no	W	System value etc. AND: Positive: power flowing from the Multi to the dc system. Negative: the other way around.
com.victronenergy.vebus	Input voltage phase 1	3	uint16	10	0 to 6553.5	/Ac/ActiveIn/L1/V	no	V AC
com.victronenergy.vebus	Input voltage phase 2	4	uint16	10	0 to 6553.5	/Ac/ActiveIn/L2/V	no	V AC
com.victronenergy.vebus	Input voltage phase 3	5	uint16	10	0 to 6553.5	/Ac/ActiveIn/L3/V	no	V AC
com.victronenergy.vebus	Input current phase 1	6	int16	10	-3276.8 to 3276.7	/Ac/ActiveIn/L1/I	no	A AC	Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
com.victronenergy.vebus	Input current phase 2	7	int16	10	-3276.8 to 3276.7	/Ac/ActiveIn/L2/I	no	A AC	Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
com.victronenergy.vebus	Input current phase 3	8	int16	10	-3276.8 to 3276.7	/Ac/ActiveIn/L3/I	no	A AC	Positive: current flowing from mains to Multi. Negative: current flowing from Multi to mains.
com.victronenergy.vebus	Input frequency 1	9	int16	100	-327.68 to 327.67	/Ac/ActiveIn/L1/F	no	Hz
com.victronenergy.vebus	Input frequency 2	10	int16	100	-327.68 to 327.67	/Ac/ActiveIn/L2/F	no	Hz
com.victronenergy.vebus	Input frequency 3	11	int16	100	-327.68 to 327.67	/Ac/ActiveIn/L3/F	no	Hz
com.victronenergy.vebus	Input power 1	12	int16	0,1	-327680 to 327670	/Ac/ActiveIn/L1/P	no	VA or Watts	Sign meaning equal to Input current
com.victronenergy.vebus	Input power 2	13	int16	0,1	-327680 to 327670	/Ac/ActiveIn/L2/P	no	VA or Watts	Sign meaning equal to Input current
com.victronenergy.vebus	Input power 3	14	int16	0,1	-327680 to 327670	/Ac/ActiveIn/L3/P	no	VA or Watts	Sign meaning eaqual to Input current
com.victronenergy.vebus	Output voltage phase 1	15	uint16	10	0 to 6553.5	/Ac/Out/L1/V	no	V AC
com.victronenergy.vebus	Output voltage phase 2	16	uint16	10	0 to 6553.5	/Ac/Out/L2/V	no	V AC
com.victronenergy.vebus	Output voltage phase 3	17	uint16	10	0 to 6553.5	/Ac/Out/L3/V	no	V AC
com.victronenergy.vebus	Output current phase 1	18	int16	10	-3276.8 to 3276.7	/Ac/Out/L1/I	no	A AC	Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
com.victronenergy.vebus	Output current phase 2	19	int16	10	-3276.8 to 3276.7	/Ac/Out/L2/I	no	A AC	Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
com.victronenergy.vebus	Output current phase 3	20	int16	10	-3276.8 to 3276.7	/Ac/Out/L3/I	no	A AC	Postive: current flowing from Multi to the load. Negative: current flowing from load to the Multi.
com.victronenergy.vebus	Output frequency	21	int16	100	-327.68 to 327.67	/Ac/Out/L1/F	no	Hz
com.victronenergy.vebus	Active input current limit	22	int16	10	-3276.8 to 3276.7	/Ac/ActiveIn/CurrentLimit	yes	A	See Venus-OS manual for limitations, for example when VE.Bus BMS or DMC is installed.
com.victronenergy.vebus	Output power 1	23	int16	0,1	-327680 to 327670	/Ac/Out/L1/P	no	VA or Watts	Sign meaning equal to Output current
com.victronenergy.vebus	Output power 2	24	int16	0,1	-327680 to 327670	/Ac/Out/L2/P	no	VA or Watts	Sign meaning equal to Output current
com.victronenergy.vebus	Output power 3	25	int16	0,1	-327680 to 327670	/Ac/Out/L3/P	no	VA or Watts	Sign meaning equal to Output current
com.victronenergy.vebus	Battery voltage	26	uint16	100	0 to 655.35	/Dc/0/Voltage	no	V DC
com.victronenergy.vebus	Battery current	27	int16	10	-3276.8 to 3276.7	/Dc/0/Current	no	A DC	Positive: current flowing from the Multi to the dc system. Negative: the other way around.
com.victronenergy.vebus	Phase count	28	uint16	1	0 to 65536	/Ac/NumberOfPhases	no	count
com.victronenergy.vebus	Active input	29	uint16	1	0 to 65536	/Ac/ActiveIn/ActiveInput	no	0=AC Input 1;1=AC Input 2;240=Disconnected
com.victronenergy.vebus	VE.Bus state of charge	30	uint16	10	0 to 6553.5	/Soc	yes	%
com.victronenergy.vebus	VE.Bus state	31	uint16	1	0 to 65536	/State	no	0=Off;1=Low Power;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply;252=Bulk protection
com.victronenergy.vebus	VE.Bus Error	32	uint16	1	0 to 65536	/VebusError	no	0=No error;1=VE.Bus Error 1: Device is switched off because one of the other phases in the system has switched off;2=VE.Bus Error 2: New and old types MK2 are mixed in the system;3=VE.Bus Error 3: Not all- or more than- the expected devices were found in the system;4=VE.Bus Error 4: No other device whatsoever detected;5=VE.Bus Error 5: Overvoltage on AC-out;6=VE.Bus Error 6: Error in DDC Program;7=VE.Bus BMS connected- which requires an Assistant- but no assistant found;10=VE.Bus Error 10: System time synchronisation problem occurred;14=VE.Bus Error 14: Device cannot transmit data;16=VE.Bus Error 16: Dongle missing;17=VE.Bus Error 17: One of the devices assumed master status because the original master failed;18=VE.Bus Error 18: AC Overvoltage on the output of a slave has occurred while already switched off;22=VE.Bus Error 22: This device cannot function as slave;24=VE.Bus Error 24: Switch-over system protection initiated;25=VE.Bus Error 25: Firmware incompatibility. The firmware of one of the connected device is not sufficiently up to date to operate in conjunction with this device;26=VE.Bus Error 26: Internal error
com.victronenergy.vebus	Switch Position	33	uint16	1	0 to 65536	/Mode	yes	1=Charger Only;2=Inverter Only;3=On;4=Off	See Venus-OS manual for limitations, for example when VE.Bus BMS or DMC is installed.
com.victronenergy.vebus	Temperature alarm	34	uint16	1	0 to 65536	/Alarms/HighTemperature	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Low battery alarm	35	uint16	1	0 to 65536	/Alarms/LowBattery	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Overload alarm	36	uint16	1	0 to 65536	/Alarms/Overload	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	ESS power setpoint phase 1	37	int16	1	-32768 to 32767	/Hub4/L1/AcPowerSetpoint	yes	W	ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
com.victronenergy.vebus	ESS disable charge flag phase	38	uint16	1	0 to 65536	/Hub4/DisableCharge	yes	0=Charge allowed;1=Charge disabled	ESS Mode 3 - Enables/Disables charge (0=enabled, 1=disabled). Note that power setpoint will yield to this setting
com.victronenergy.vebus	ESS disable feedback flag phase	39	uint16	1	0 to 65536	/Hub4/DisableFeedIn	yes	0=Feed in allowed;1=Feed in disabled	ESS Mode 3 - Enables/Disables feedback (0=enabled, 1=disabled). Note that power setpoint will yield to this setting
com.victronenergy.vebus	ESS power setpoint phase 2	40	int16	1	-32768 to 32767	/Hub4/L2/AcPowerSetpoint	yes	W	ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
com.victronenergy.vebus	ESS power setpoint phase 3	41	int16	1	-32768 to 32767	/Hub4/L3/AcPowerSetpoint	yes	W	ESS Mode 3 - Instructs the multi to charge/discharge with giving power. Negative = discharge. Used by the control loop in grid-parallel systems.
com.victronenergy.vebus	Temperatur sensor alarm	42	uint16	1	0 to 65536	/Alarms/TemperatureSensor	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Voltage sensor alarm	43	uint16	1	0 to 65536	/Alarms/VoltageSensor	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Temperature alarm L1	44	uint16	1	0 to 65536	/Alarms/L1/HighTemperature	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Low battery alarm L1	45	uint16	1	0 to 65536	/Alarms/L1/LowBattery	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Overload alarm L1	46	uint16	1	0 to 65536	/Alarms/L1/Overload	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Ripple alarm L1	47	uint16	1	0 to 65536	/Alarms/L1/Ripple	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Temperature alarm L2	48	uint16	1	0 to 65536	/Alarms/L2/HighTemperature	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Low battery alarm L2	49	uint16	1	0 to 65536	/Alarms/L2/LowBattery	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Overload alarm L2	50	uint16	1	0 to 65536	/Alarms/L2/Overload	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Ripple alarm L2	51	uint16	1	0 to 65536	/Alarms/L2/Ripple	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Temperature alarm L3	52	uint16	1	0 to 65536	/Alarms/L3/HighTemperature	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Low battery alarm L3	53	uint16	1	0 to 65536	/Alarms/L3/LowBattery	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Overload alarm L3	54	uint16	1	0 to 65536	/Alarms/L3/Overload	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Ripple alarm L3	55	uint16	1	0 to 65536	/Alarms/L3/Ripple	no	0=Ok;1=Warning;2=Alarm
com.victronenergy.vebus	Disable PV inverter	56	uint16	1	0 to 65536	/PvInverter/Disable	yes	0=PV enabled;1=PV disabled	Disable PV inverter on AC out (using frequency shifting). Only works when vebus device is in inverter mode. Needs ESS or PV inverter assistant
com.victronenergy.vebus	VE.Bus BMS allows battery to be charged	57	uint16	1	0 to 65536	/Bms/AllowToCharge	no	0=No;1=Yes	VE.Bus BMS allows the battery to be charged
com.victronenergy.vebus	VE.Bus BMS allows battery to be discharged	58	uint16	1	0 to 65536	/Bms/AllowToDischarge	no	0=No;1=Yes	VE.Bus BMS allows the battery to be discharged
com.victronenergy.vebus	VE.Bus BMS is expected	59	uint16	1	0 to 65536	/Bms/BmsExpected	no	0=No;1=Yes	Presence of VE.Bus BMS is expected based on vebus settings (presence of ESS or BMS assistant)
com.victronenergy.vebus	VE.Bus BMS error	60	uint16	1	0 to 65536	/Bms/Error	no	0=No;1=Yes
com.victronenergy.vebus	Battery temperature	61	int16	10	-3276.8 to 3276.7	/Dc/0/Temperature	no	Degrees celsius
com.victronenergy.vebus	VE.Bus Reset	62	uint16	1	0 to 65536	/SystemReset	yes	1=VE.Bus reset	Any write action will cause a reset
com.victronenergy.vebus	Phase rotation warning	63	uint16	1	0 to 65536	/Alarms/PhaseRotation	no	0=Ok;1=Warning
com.victronenergy.vebus	Grid lost alarm	64	uint16	1	0 to 65536	/Alarms/GridLost	no	0=Ok;2=Alarm
com.victronenergy.vebus	Feed DC overvoltage into grid	65	uint16	1	0 to 65536	/Hub4/DoNotFeedInOvervoltage	yes	0=Feed in overvoltage;1=Do not feed in overvoltage
com.victronenergy.vebus	Maximum overvoltage feed-in power L1	66	uint16	0,01	0 to 6553600	/Hub4/L1/MaxFeedInPower	yes	W
com.victronenergy.vebus	Maximum overvoltage feed-in power L2	67	uint16	0,01	0 to 6553600	/Hub4/L2/MaxFeedInPower	yes	W
com.victronenergy.vebus	Maximum overvoltage feed-in power L3	68	uint16	0,01	0 to 6553600	/Hub4/L3/MaxFeedInPower	yes	W
com.victronenergy.battery	Battery voltage	259	uint16	100	0 to 655.35	/Dc/0/Voltage	no	V DC
com.victronenergy.battery	Starter battery voltage	260	uint16	100	0 to 655.35	/Dc/1/Voltage	no	V DC
com.victronenergy.battery	Current	261	int16	10	-3276.8 to 3276.7	/Dc/0/Current	no	A DC	Postive: battery begin charged. Negative: battery being discharged
com.victronenergy.battery	Battery temperature	262	int16	10	-3276.8 to 3276.7	/Dc/0/Temperature	no	Degrees celsius	In degrees Celsius
com.victronenergy.battery	Mid-point voltage of the battery bank	263	uint16	100	0 to 655.35	/Dc/0/MidVoltage	no	V DC
com.victronenergy.battery	Mid-point deviation of the battery bank	264	uint16	100	0 to 655.35	/Dc/0/MidVoltageDeviation	no	%
com.victronenergy.battery	Consumed Amphours	265	uint16	-10	0 to -6553.6	/ConsumedAmphours	no	Ah	Always negative (to have the same sign as the current).
com.victronenergy.battery	State of charge	266	uint16	10	0 to 6553.6	/Soc	no	%
com.victronenergy.battery	Alarm	267	uint16	1	0 to 65536	/Alarms/Alarm	no	0=No alarm;2=Alarm	2015-01-19: Deprecated for CCGX. Value is always 0.
com.victronenergy.battery	Low voltage alarm	268	uint16	1	0 to 65536	/Alarms/LowVoltage	no	0=No alarm;2=Alarm
com.victronenergy.battery	High voltage alarm	269	uint16	1	0 to 65536	/Alarms/HighVoltage	no	0=No alarm;2=Alarm
com.victronenergy.battery	Low starter-voltage alarm	270	uint16	1	0 to 65536	/Alarms/LowStarterVoltage	no	0=No alarm;2=Alarm
com.victronenergy.battery	High starter-voltage alarm	271	uint16	1	0 to 65536	/Alarms/HighStarterVoltage	no	0=No alarm;2=Alarm
com.victronenergy.battery	Low State-of-charge alarm	272	uint16	1	0 to 65536	/Alarms/LowSoc	no	0=No alarm;2=Alarm
com.victronenergy.battery	Low temperature alarm	273	uint16	1	0 to 65536	/Alarms/LowTemperature	no	0=No alarm;2=Alarm
com.victronenergy.battery	High temperature alarm	274	uint16	1	0 to 65536	/Alarms/HighTemperature	no	0=No alarm;2=Alarm
com.victronenergy.battery	Mid-voltage alarm	275	uint16	1	0 to 65536	/Alarms/MidVoltage	no	0=No alarm;2=Alarm
com.victronenergy.battery	Low fused-voltage alarm	276	uint16	1	0 to 65536	/Alarms/LowFusedVoltage	no	0=No alarm;2=Alarm	2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery	High fused-voltage alarm	277	uint16	1	0 to 65536	/Alarms/HighFusedVoltage	no	0=No alarm;2=Alarm	2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery	Fuse blown alarm	278	uint16	1	0 to 65536	/Alarms/FuseBlown	no	0=No alarm;2=Alarm
com.victronenergy.battery	High internal-temperature alarm	279	uint16	1	0 to 65536	/Alarms/HighInternalTemperature	no	0=No alarm;2=Alarm
com.victronenergy.battery	Relay status	280	uint16	1	0 to 65536	/Relay/0/State	yes	0=Open;1=Closed	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Deepest discharge	281	uint16	-10	0 to -6553.6	/History/DeepestDischarge	no	Ah	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Last discharge	282	uint16	-10	0 to -6553.6	/History/LastDischarge	no	Ah	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Average discharge	283	uint16	-10	0 to -6553.6	/History/AverageDischarge	no	Ah	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Charge cycles	284	uint16	1	0 to 65536	/History/ChargeCycles	no	count	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Full discharges	285	uint16	1	0 to 65536	/History/FullDischarges	no	count	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Total Ah drawn	286	uint16	-10	0 to -6553.6	/History/TotalAhDrawn	no	Ah	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Minimum voltage	287	uint16	100	0 to 655.35	/History/MinimumVoltage	no	V DC	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Maximum voltage	288	uint16	100	0 to 655.35	/History/MaximumVoltage	no	V DC	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Time since last full charge	289	uint16	0,01	0 to 6553600	/History/TimeSinceLastFullCharge	no	seconds	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Automatic syncs	290	uint16	1	0 to 65536	/History/AutomaticSyncs	no	count	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Low voltage alarms	291	uint16	1	0 to 65536	/History/LowVoltageAlarms	no	count	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	High voltage alarms	292	uint16	1	0 to 65536	/History/HighVoltageAlarms	no	count	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Low starter voltage alarms	293	uint16	1	0 to 65536	/History/LowStarterVoltageAlarms	no	count	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	High starter voltage alarms	294	uint16	1	0 to 65536	/History/HighStarterVoltageAlarms	no	count	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Minimum starter voltage	295	uint16	100	0 to 655.35	/History/MinimumStarterVoltage	no	V DC	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Maximum starter voltage	296	uint16	100	0 to 655.35	/History/MaximumStarterVoltage	no	V DC	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Low fused-voltage alarms	297	uint16	1	0 to 65536	/History/LowFusedVoltageAlarms	no	count	2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery	High fused-voltage alarms	298	uint16	1	0 to 65536	/History/HighFusedVoltageAlarms	no	count	2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery	Minimum fused voltage	299	uint16	100	0 to 655.35	/History/MinimumFusedVoltage	no	V DC	2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery	Maximum fused voltage	300	uint16	100	0 to 655.35	/History/MaximumFusedVoltage	no	V DC	2014-12-13: Deprecated because over-engineered. Value is always 0.
com.victronenergy.battery	Discharged Energy	301	uint16	10	0 to 6553.5	/History/DischargedEnergy	no	kWh	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Charged Energy	302	uint16	10	0 to 6553.5	/History/ChargedEnergy	no	kWh	Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	Time to go	303	uint16	0,01	0 to 6553600	/TimeToGo	no	seconds	Special value: 0 = charging. Not supported by CAN.Bus BMS batteries.
com.victronenergy.battery	State of health	304	uint16	10	0 to 6553.5	/Soh	no	%	Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery	Max charge voltage	305	uint16	10	0 to 6553.5	/Info/MaxChargeVoltage	no	V DC	Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery	Min discharge voltage	306	uint16	10	0 to 6553.5	/Info/BatteryLowVoltage	no	V DC	Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery	Max charge current	307	uint16	10	0 to 6553.5	/Info/MaxChargeCurrent	no	A DC	Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery	Max discharge current	308	uint16	10	0 to 6553.5	/Info/MaxDischargeCurrent	no	A DC	Not supported by Victron products. Supported by CAN.Bus batteries.
com.victronenergy.battery	Capacity	309	uint16	10	0 to 6553.5	/Capacity	no	Ah
com.victronenergy.battery	Diagnostics; 1st last error timestamp	310	int32	1	-2147483648 to 2147483648	/Diagnostics/LastErrors/1/Time	no
com.victronenergy.battery	Diagnostics; 2nd last error timestamp	312	int32	1	-2147483648 to 2147483648	/Diagnostics/LastErrors/2/Time	no
com.victronenergy.battery	Diagnostics; 3rd last error timestamp	314	int32	1	-2147483648 to 2147483648	/Diagnostics/LastErrors/3/Time	no
com.victronenergy.battery	Diagnostics; 4th last error timestamp	316	int32	1	-2147483648 to 2147483648	/Diagnostics/LastErrors/4/Time	no
com.victronenergy.battery	Minimum cell temperature	318	int16	10	-3276.8 to 3276.7	/System/MinCellTemperature	no	Degrees celsius
com.victronenergy.battery	Maximum cell temperature	319	int16	10	-3276.8 to 3276.7	/System/MaxCellTemperature	no	Degrees celsius
com.victronenergy.battery	High charge current alarm	320	uint16	1	0 to 65536	/Alarms/HighChargeCurrent	no	0=No alarm;2=Alarm
com.victronenergy.battery	High discharge current alarm	321	uint16	1	0 to 65536	/Alarms/HighDischargeCurrent	no	0=No alarm;2=Alarm
com.victronenergy.battery	Cell imbalance alarm	322	uint16	1	0 to 65536	/Alarms/CellImbalance	no	0=No alarm;2=Alarm
com.victronenergy.battery	Internal failure alarm	323	uint16	1	0 to 65536	/Alarms/InternalFailure	no	0=No alarm;2=Alarm
com.victronenergy.battery	High charge temperature alarm	324	uint16	1	0 to 65536	/Alarms/HighChargeTemperature	no	0=No alarm;2=Alarm
com.victronenergy.battery	Low charge temperature alarm	325	uint16	1	0 to 65536	/Alarms/LowChargeTemperature	no	0=No alarm;2=Alarm
com.victronenergy.battery	Low cell voltage alarm	326	uint16	1	0 to 65536	/Alarms/LowCellVoltage	no	0=No alarm;1=Almost discharged;2=Alarm
com.victronenergy.solarcharger	Battery voltage	771	uint16	100	0 to 655.35	/Dc/0/Voltage	no	V DC
com.victronenergy.solarcharger	Battery current	772	int16	10	-3276.8 to 3276.7	/Dc/0/Current	no	A DC
com.victronenergy.solarcharger	Battery temperature	773	int16	10	-3276.8 to 3276.7	/Dc/0/Temperature	no	Degrees celsius	VE.Can MPPTs only
com.victronenergy.solarcharger	Charger on/off	774	uint16	1	0 to 65536	/Mode	yes	1=On;4=Off	VE.Can MPPTs only
com.victronenergy.solarcharger	Charge state	775	uint16	1	0 to 65536	/State	no	0=Off;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;11=Other (Hub-1);252=External control
com.victronenergy.solarcharger	PV voltage	776	uint16	100	0 to 655.35	/Pv/V	no	V DC	Not available if multiple VE.Can chargers are combined
com.victronenergy.solarcharger	PV current	777	int16	10	-3276.8 to 3276.7	/Pv/I	no	A DC	Not available if multiple VE.Can chargers are combined
com.victronenergy.solarcharger	Equalization pending	778	uint16	1	0 to 65536	/Equalization/Pending	no	0=No;1=Yes;2=Error;3=Unavailable- Unknown
com.victronenergy.solarcharger	Equalization time remaining	779	uint16	10	0 to 6553.5	/Equalization/TimeRemaining	no	seconds
com.victronenergy.solarcharger	Relay on the charger	780	uint16	1	0 to 65536	/Relay/0/State	no	0=Open;1=Closed
com.victronenergy.solarcharger		781	uint16	1	0 to 65536	/Alarms/Alarm	no	0=No alarm;2=Alarm	Deprecated. Value is always 0
com.victronenergy.solarcharger	Low batt. voltage alarm	782	uint16	1	0 to 65536	/Alarms/LowVoltage	no	0=No alarm;2=Alarm
com.victronenergy.solarcharger	High batt. voltage alarm	783	uint16	1	0 to 65536	/Alarms/HighVoltage	no	0=No alarm;2=Alarm
com.victronenergy.solarcharger	Yield today	784	uint16	10	0 to 6553.5	/History/Daily/0/Yield	no	kWh	Today's yield
com.victronenergy.solarcharger	Maximum charge power today	785	uint16	1	0 to 65536	/History/Daily/0/MaxPower	no	W	Today's maximum power
com.victronenergy.solarcharger	Yield yesterday	786	uint16	10	0 to 6553.5	/History/Daily/1/Yield	no	kWh	Yesterday's yield
com.victronenergy.solarcharger	Maximum charge power yesterday	787	uint16	1	0 to 65536	/History/Daily/1/MaxPower	no	W	Yesterday's maximum power
com.victronenergy.solarcharger	Error code	788	uint16	1	0 to 65536	/ErrorCode	no	0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
com.victronenergy.solarcharger	PV power	789	uint16	10	0 to 6553.5	/Yield/Power	no	W
com.victronenergy.solarcharger	User yield	790	uint16	10	0 to 6553.5	/Yield/User	no	kWh	Energy generated by the solarcharger since last user reset
com.victronenergy.solarcharger	MPP operation mode	791	uint16	1	0 to 65536	/MppOperationMode	no	0=Off;1=Voltage/current limited;2=MPPT active;255=Not available
com.victronenergy.pvinverter	Position	1026	uint16	1	0 to 65536	/Position	no	0=AC input 1;1=AC output;2=AC input 2
com.victronenergy.pvinverter	L1 Voltage	1027	uint16	10	0 to 6553.5	/Ac/L1/Voltage	no	V AC
com.victronenergy.pvinverter	L1 Current	1028	int16	10	-3276.8 to 3276.7	/Ac/L1/Current	no	A AC
com.victronenergy.pvinverter	L1 Power	1029	uint16	1	0 to 65536	/Ac/L1/Power	no	W
com.victronenergy.pvinverter	L1 Energy	1030	uint16	100	0 to 655.35	/Ac/L1/Energy/Forward	no	kWh	Deprecated. Use 1046 instead.
com.victronenergy.pvinverter	L2 Voltage	1031	uint16	10	0 to 6553.5	/Ac/L2/Voltage	no	V AC
com.victronenergy.pvinverter	L2 Current	1032	int16	10	-3276.8 to 3276.7	/Ac/L2/Current	no	A AC
com.victronenergy.pvinverter	L2 Power	1033	uint16	1	0 to 65536	/Ac/L2/Power	no	W
com.victronenergy.pvinverter	L2 Energy	1034	uint16	100	0 to 655.35	/Ac/L2/Energy/Forward	no	kWh	Deprecated. Use 1048 instead.
com.victronenergy.pvinverter	L3 Voltage	1035	uint16	10	0 to 6553.5	/Ac/L3/Voltage	no	V AC
com.victronenergy.pvinverter	L3 Current	1036	int16	10	-3276.8 to 3276.7	/Ac/L3/Current	no	A AC
com.victronenergy.pvinverter	L3 Power	1037	uint16	1	0 to 65536	/Ac/L3/Power	no	W
com.victronenergy.pvinverter	L3 Energy	1038	uint16	100	0 to 655.35	/Ac/L3/Energy/Forward	no	kWh	Deprecated. Use 1050 instead.
com.victronenergy.pvinverter	Serial	1039	string[7]	1	Max 14 characters	/Serial	no		The system serial as string (MSB of first register: first character, LSB of last register: last character).
com.victronenergy.pvinverter	L1 Energy	1046	uint32	100	0 to 42949672.96	/Ac/L1/Energy/Forward	no	kWh
com.victronenergy.pvinverter	L2 Energy	1048	uint32	100	0 to 42949672.96	/Ac/L2/Energy/Forward	no	kWh
com.victronenergy.pvinverter	L3 Energy	1050	uint32	100	0 to 42949672.96	/Ac/L3/Energy/Forward	no	kWh
com.victronenergy.battery	State	1282	uint16	1	0 to 65536	/State	no	0=Initializing (Wait start);1=Initializing (before boot);2=Initializing (Before boot delay);3=Initializing (Wait boot);4=Initializing;5=Initializing (Measure battery voltage);6=Initializing (Calculate battery voltage);7=Initializing (Wait bus voltage);8=Initializing (Wait for lynx shunt);9=Running;10=Error (10);11=Error (11)
com.victronenergy.battery	Error	1283	uint16	1	0 to 65536	/ErrorCode	no	0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable
com.victronenergy.battery	System-switch	1284	uint16	1	0 to 65536	/SystemSwitch	no	0=Disabled;1=Enabled
com.victronenergy.battery	Balancing	1285	uint16	1	0 to 65536	/Balancing	no	0=Inactive;1=Active
com.victronenergy.battery	System; number of batteries	1286	uint16	1	0 to 65536	/System/NrOfBatteries	no	count
com.victronenergy.battery	System; batteries parallel	1287	uint16	1	0 to 65536	/System/BatteriesParallel	no	count
com.victronenergy.battery	System; batteries series	1288	uint16	1	0 to 65536	/System/BatteriesSeries	no	count
com.victronenergy.battery	System; number of cells per battery	1289	uint16	1	0 to 65536	/System/NrOfCellsPerBattery	no	count
com.victronenergy.battery	System; minimum cell voltage	1290	uint16	100	0 to 655.35	/System/MinCellVoltage	no	V DC
com.victronenergy.battery	System; maximum cell voltage	1291	uint16	100	0 to 655.35	/System/MaxCellVoltage	no	V DC
com.victronenergy.battery	Diagnostics; shutdowns due to error	1292	uint16	1	0 to 65536	/Diagnostics/ShutDownsDueError	no	count
com.victronenergy.battery	Diagnostics; 1st last error	1293	uint16	1	0 to 65536	/Diagnostics/LastErrors/1/Error	no	0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable
com.victronenergy.battery	Diagnostics; 2nd last error	1294	uint16	1	0 to 65536	/Diagnostics/LastErrors/2/Error	no	0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable
com.victronenergy.battery	Diagnostics; 3rd last error	1295	uint16	1	0 to 65536	/Diagnostics/LastErrors/3/Error	no	0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable
com.victronenergy.battery	Diagnostics; 4th last error	1296	uint16	1	0 to 65536	/Diagnostics/LastErrors/4/Error	no	0=No error;1=Battery initialization error;2=No batteries connected;3=Unknown battery connected;4=Different battery type;5=Number of batteries incorrect;6=Lynx Shunt not found;7=Battery measure error;8=Internal calculation error;9=Batteries in series not ok;10=Number of batteries incorrect;11=Hardware error;12=Watchdog error;13=Over voltage;14=Under voltage;15=Over temperature;16=Under temperature;17=Hardware fault;18=Standby shutdown;19=Pre-charge charge error;20=Safety contactor check error;21=Pre-charge discharge error;22=ADC error;23=Slave error;24=Slave warning;25=Pre-charge error;26=Safety contactor error;27=Over current;28=Slave update failed;29=Slave update unavailable
com.victronenergy.battery	IO; allow to charge	1297	uint16	1	0 to 65536	/Io/AllowToCharge	no	0=No;1=Yes
com.victronenergy.battery	IO; allow to discharge	1298	uint16	1	0 to 65536	/Io/AllowToDischarge	no	0=No;1=Yes
com.victronenergy.battery	IO; external relay	1299	uint16	1	0 to 65536	/Io/ExternalRelay	no	0=Inactive;1=Active
com.victronenergy.battery	History; Min cell-voltage	1300	uint16	100	0 to 655.35	/History/MinimumCellVoltage	no	V DC
com.victronenergy.battery	History; Max cell-voltage	1301	uint16	100	0 to 655.35	/History/MaximumCellVoltage	no	V DC
com.victronenergy.motordrive	Motor RPM	2048	int16	1	-32768 to 32767	/Motor/RPM	no	RPM
com.victronenergy.motordrive	Motor temperature	2049	int16	10	-3276.8 to 3276.7	/Motor/Temperature	no	Degrees celsius
com.victronenergy.motordrive	Controller DC Voltage	2050	uint16	100	0 to 655.35	/Dc/0/Voltage	no	V DC
com.victronenergy.motordrive	Controller DC Current	2051	int16	10	-3276.8 to 3276.7	/Dc/0/Current	no	A DC
com.victronenergy.motordrive	Controller DC Power	2052	int16	10	-3276.8 to 3276.7	/Dc/0/Power	no	W	Positive = being powered from battery, Negative is charging battery (regeneration)
com.victronenergy.motordrive	Controller Temperature	2053	int16	10	-3276.8 to 3276.7	/Controller/Temperature	no	Degrees celsius
com.victronenergy.charger	Output 1 - voltage	2307	uint16	100	0 to 655.35	/Dc/0/Voltage	no	V DC
com.victronenergy.charger	Output 1 - current	2308	int16	10	-3276.8 to 3276.7	/Dc/0/Current	no	A DC
com.victronenergy.charger	Output 1 - temperature	2309	int16	10	-3276.8 to 3276.7	/Dc/0/Temperature	no	Degrees celsius
com.victronenergy.charger	Output 2 - voltage	2310	uint16	100	0 to 655.35	/Dc/1/Voltage	no	V DC
com.victronenergy.charger	Output 2 - current	2311	int16	10	-3276.8 to 3276.7	/Dc/1/Current	no	A DC
com.victronenergy.charger	Output 3 - voltage	2312	uint16	100	0 to 655.35	/Dc/2/Voltage	no	V DC
com.victronenergy.charger	Output 3 - current	2313	int16	10	-3276.8 to 3276.7	/Dc/2/Current	no	A DC
com.victronenergy.charger	AC Current	2314	int16	10	-3276.8 to 3276.7	/Ac/In/L1/I	no	A AC
com.victronenergy.charger	AC Power	2315	uint16	1	0 to 65536	/Ac/In/L1/P	no	W DC
com.victronenergy.charger	AC Current limit	2316	int16	10	-3276.8 to 3276.7	/Ac/In/CurrentLimit	yes	A AC
com.victronenergy.charger	Charger on/off	2317	uint16	1	0 to 65536	/Mode	yes	0=Off;1=On;2=Error;3=Unavailable- Unknown
com.victronenergy.charger	Charge state	2318	uint16	1	0 to 65536	/State	no	0=Off;1=Low Power Mode;2=Fault;3=Bulk;4=Absorption;5=Float;6=Storage;7=Equalize;8=Passthru;9=Inverting;10=Power assist;11=Power supply mode;252=Bulk protection
com.victronenergy.charger	Error code	2319	uint16	1	0 to 65536	/ErrorCode	no	0=No error;1=Battery temperature too high;2=Battery voltage too high;3=Battery temperature sensor miswired (+);4=Battery temperature sensor miswired (-);5=Battery temperature sensor disconnected;6=Battery voltage sense miswired (+);7=Battery voltage sense miswired (-);8=Battery voltage sense disconnected;9=Battery voltage wire losses too high;17=Charger temperature too high;18=Charger over-current;19=Charger current polarity reversed;20=Bulk time limit reached;22=Charger temperature sensor miswired;23=Charger temperature sensor disconnected;34=Input current too high
com.victronenergy.charger	Relay on the charger	2320	uint16	1	0 to 65536	/Relay/0/State	no	0=Open;1=Closed
com.victronenergy.charger	Low voltage alarm	2321	uint16	1	0 to 65536	/Alarms/LowVoltage	no	0=No alarm;2=Alarm
com.victronenergy.charger	High voltage alarm	2322	uint16	1	0 to 65536	/Alarms/HighVoltage	no	0=No alarm;2=Alarm
com.victronenergy.grid	Grid L1 - Power	2600	int16	1	-32768 to 32767	/Ac/L1/Power	no	W
com.victronenergy.grid	Grid L2 - Power	2601	int16	1	-32768 to 32767	/Ac/L2/Power	no	W
com.victronenergy.grid	Grid L3 - Power	2602	int16	1	-32768 to 32767	/Ac/L3/Power	no	W
com.victronenergy.grid	Grid L1 - Energy from net	2603	uint16	100	0 to 655.35	/Ac/L1/Energy/Forward	no	kWh
com.victronenergy.grid	Grid L2 - Energy from net	2604	uint16	100	0 to 655.35	/Ac/L2/Energy/Forward	no	kWh
com.victronenergy.grid	Grid L3 - Energy from net	2605	uint16	100	0 to 655.35	/Ac/L3/Energy/Forward	no	kWh
com.victronenergy.grid	Grid L1 - Energy to net	2606	uint16	100	0 to 655.35	/Ac/L1/Energy/Reverse	no	kWh
com.victronenergy.grid	Grid L2 - Energy to net	2607	uint16	100	0 to 655.35	/Ac/L2/Energy/Reverse	no	kWh
com.victronenergy.grid	Grid L3 - Energy to net	2608	uint16	100	0 to 655.35	/Ac/L3/Energy/Reverse	no	kWh
com.victronenergy.grid	Serial	2609	string[7]		14 characters	/Serial	no		The grid meter serial as string (MSB of first register: first character, LSB of last register: last character).
com.victronenergy.grid	Grid L1 – Voltage	2616	uint16	10	0 to 6553.5	/Ac/L1/Voltage	no	V AC
com.victronenergy.grid	Grid L1 – Current	2617	int16	10	-3276.8 to 3276.7	/Ac/L1/Current	no	A AC
com.victronenergy.grid	Grid L2 – Voltage	2618	uint16	10	0 to 6553.5	/Ac/L2/Voltage	no	V AC
com.victronenergy.grid	Grid L2 – Current	2619	int16	10	-3276.8 to 3276.7	/Ac/L2/Current	no	A AC
com.victronenergy.grid	Grid L3 – Voltage	2620	uint16	10	0 to 6553.5	/Ac/L3/Voltage	no	V AC
com.victronenergy.grid	Grid L3 – Current	2621	int16	10	-3276.8 to 3276.7	/Ac/L3/Current	no	A AC
com.victronenergy.grid	Grid L1 - Energy from net	2622	uint32	100	0 to 42949672.96	/Ac/L1/Energy/Forward	no	kWh
com.victronenergy.grid	Grid L2 - Energy from net	2624	uint32	100	0 to 42949672.96	/Ac/L2/Energy/Forward	no	kWh
com.victronenergy.grid	Grid L3 - Energy from net	2626	uint32	100	0 to 42949672.96	/Ac/L3/Energy/Forward	no	kWh
com.victronenergy.grid	Grid L1 - Energy to net	2628	uint32	100	0 to 42949672.96	/Ac/L1/Energy/Reverse	no	kWh
com.victronenergy.grid	Grid L2 - Energy to net	2630	uint32	100	0 to 42949672.96	/Ac/L2/Energy/Reverse	no	kWh
com.victronenergy.grid	Grid L3 - Energy to net	2632	uint32	100	0 to 42949672.96	/Ac/L3/Energy/Reverse	no	kWh
com.victronenergy.settings	ESS control loop setpoint	2700	int16	1	-32768 to 32767	/Settings/Cgwacs/AcPowerSetPoint	yes	W	ESS Mode 2 - Setpoint for the ESS control-loop in the CCGX. The control-loop will increase/decrease the Multi charge/discharge power to get the grid reading to this setpoint
com.victronenergy.settings	ESS max charge current (fractional)	2701	uint16	1	0 to 100	/Settings/Cgwacs/MaxChargePercentage	yes	%	ESS Mode 2 - Max charge current for ESS control-loop. The control-loop will use this value to limit the multi power setpoint. For DVCC, use 2705 instead.
com.victronenergy.settings	ESS max discharge current (fractional)	2702	uint16	1	0 to 100	/Settings/Cgwacs/MaxDischargePercentage	yes	%	ESS Mode 2 - Max discharge current for ESS control-loop. The control-loop will use this value to limit the multi power setpoint. Currently a value < 50% will disable discharge completely. >=50% allows. Consider using 2704 instead.
com.victronenergy.settings	ESS control loop setpoint	2703	int16	0,01	-3276800 to 3276700	/Settings/Cgwacs/AcPowerSetPoint	yes	W	ESS Mode 2 – Same as 2700, but with a different scale factor. Meant for values larger than +-32kW.
com.victronenergy.settings	ESS max discharge current	2704	uint16	0,1	0 to 655360	/Settings/Cgwacs/MaxDischargePower	yes	W	ESS Mode 2 – similar to 2702, but as an absolute value instead of a percentage.
com.victronenergy.settings	DVCC system max charge current	2705	int16	1	-32768 to 32767	/Settings/SystemSetup/MaxChargeCurrent	yes	A DC	ESS Mode 2 with DVCC – Maximum system charge current. -1 Disables.
com.victronenergy.settings	Maximum System Grid Feed In	2706	int16	0,01	-3276800 to 3276700	/Settings/Cgwacs/MaxFeedInPower	yes	W	-1: No limit, >=0: limited system feed-in. Applies to DC-coupled and AC-coupled feed-in.
com.victronenergy.settings	Feed excess DC-coupled PV into grid	2707	int16	1		/Settings/Cgwacs/OvervoltageFeedIn	yes	0=Don’t feed excess DC-tied PV into grid; 1=Feed excess DC-tied PV into the grid	Also known as Overvoltage Feed-in
com.victronenergy.settings	Don’t feed excess AC-coupled PV into grid	2708	int16	1		/Settings/Cgwacs/PreventFeedback	yes	0=Feed excess AC-tied PV into grid; 1=Don’t feed excess AC-tied PV into the grid	Formerly called Fronius Zero-Feedin
com.victronenergy.hub4	Grid limiting status	2709	int16	1		/PvPowerLimiterActive	no	0=Feed-in limiting is inactive; 1=Feed-in limiting is active	Applies to both AC-coupled and DC-coupled limiting
com.victronenergy.gps	Latitude	2800	int32	10000000	-214.7483648 to 214.7483648	/Position/Latitude	no	Decimal degrees
com.victronenergy.gps	Longitude	2802	int32	10000000	-214.7483648 to 214.7483648	/Position/Longitude	no	Decimal degrees
com.victronenergy.gps	Course	2804	uint16	100	0 to 655.35	/Course	no	Degrees	Direction of movement 0-360 degrees
com.victronenergy.gps	Speed	2805	uint16	100	0 to 655.35	/Speed	no	m/s	Speed in m/s
com.victronenergy.gps	GPS fix	2806	uint16	1	0 to 65536	/Fix	no		0: no fix, 1: fix
com.victronenergy.gps	GPS number of satellites	2807	uint16	1	0 to 65536	/NrOfSatellites	no
com.victronenergy.gps	Altitude	2808	int32	10	-214748364.8 to 214748364.8	/Altitude	no	m/s
com.victronenergy.settings	ESS BatteryLife state	2900	uint16	1		/Settings/CGwacs/BatteryLife/State	yes	0=Unused, BL disabled;1=Restarting;2=Self-consumption;3=Self-consumption;4=Self-consumption;5=Discharge disabled;6=Force charge;7=Sustain;9=Keep batteries charged;10=BL Disabled;11=BL Disabled (Low SoC)	Use value 0 (disable) and 1(enable) for writing only
com.victronenergy.settings	ESS Minimum SoC (unless grid fails)	2901	uint16	10		/Settings/CGwacs/BatteryLife/MinimumSocLimit	yes	%	Same as the setting in the GUI
com.victronenergy.settings	ESS Mode	2902	uint16	1	0 to 65536	/Settings/Cgwacs/Hub4Mode	yes	1=ESS with Phase Compensation;2=ESS without phase compensation;3=Disabled/External Control
com.victronenergy.tank	Product ID	3000	uint16	1	0 to 65536	/ProductId	no
com.victronenergy.tank	Tank capacity	3001	uint32	10000	0 to 429496.7296	/Capacity	no	m3
com.victronenergy.tank	Tank fluid type	3003	uint16	1	0 to 65536	/FluidType	no	0=Fuel;1=Fresh water;2=Waste water;3=Live well;4=Oil;5=Black water (sewage)
com.victronenergy.tank	Tank level	3004	uint16	10	0 to 6553.5	/Level	no	%
com.victronenergy.tank	Tank remaining fluid	3005	uint32	10000	0 to 429496.7296	/Remaining	no	m3
com.victronenergy.tank	Tank status	3007	uint16	1	0 to 65536	/Status	no	0=OK;1=Disconnected;2=Short circuited;3=Reverse Polarity;4=Unknown
com.victronenergy.inverter	Output current	3100	int16	10	-3276.8 to 3276.8	/Ac/Out/L1/I	no	A AC
com.victronenergy.inverter	Output voltage	3101	uint16	10	0 to 6553.6	/Ac/Out/L1/V	no	V AC
com.victronenergy.inverter	Battery voltage	3105	uint16	100	0 to 655.36	/Dc/0/Voltage	no	V DC
com.victronenergy.inverter	High temperature alarm	3110	uint16	1	0 to 65536	/Alarms/HighTemperature	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	High battery voltage alarm	3111	uint16	1	0 to 65536	/Alarms/HighVoltage	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	High AC-Out voltage alarm	3112	uint16	1	0 to 65536	/Alarms/HighVoltageAcOut	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	Low temperature alarm	3113	uint16	1	0 to 65536	/Alarms/LowTemperature	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	Low battery voltage alarm	3114	uint16	1	0 to 65536	/Alarms/LowVoltage	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	Low AC-Out voltage alarm	3115	uint16	1	0 to 65536	/Alarms/LowVoltageAcOut	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	Overload alarm	3116	uint16	1	0 to 65536	/Alarms/Overload	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	Ripple alarm	3117	uint16	1	0 to 65536	/Alarms/Ripple	no	0=No alarm;1=Warning;2=Alarm
com.victronenergy.inverter	Firmware version	3125	uint16	1	0 to 65536	/FirmwareVersion	no
com.victronenergy.inverter	Inverter on/off/eco	3126	uint16	1	0 to 65536	/Mode	yes	2=On;4=Off;5=Eco
com.victronenergy.inverter	Inverter model	3127	uint16	1	0 to 65536	/ProductId	no
com.victronenergy.inverter	Inverter state	3128	uint16	1	0 to 65536	/State	no	0=Off;1=Low power mode (search mode);2=Fault;9=Inverting (on)
com.victronenergy.genset	Phase 1 voltage	3200	uint16	10	0 to 6553.6	/Ac/L1/Voltage	no	V AC
com.victronenergy.genset	Phase 2 voltage	3201	uint16	10	0 to 6553.6	/Ac/L2/Voltage	no	V AC
com.victronenergy.genset	Phase 3 voltage	3202	uint16	10	0 to 6553.6	/Ac/L3/Voltage	no	V AC
com.victronenergy.genset	Phase 1 current	3203	int16	10	-3276.8 to 3276.8	/Ac/L1/Current	no	A AC
com.victronenergy.genset	Phase 2 current	3204	int16	10	-3276.8 to 3276.8	/Ac/L2/Current	no	A AC
com.victronenergy.genset	Phase 3 current	3205	int16	10	-3276.8 to 3276.8	/Ac/L3/Current	no	A AC
com.victronenergy.genset	Phase 1 power	3206	int16	1	-32768 to 32768	/Ac/L1/Power	no	W
com.victronenergy.genset	Phase 2 power	3207	int16	1	-32768 to 32768	/Ac/L2/Power	no	W
com.victronenergy.genset	Phase 3 power	3208	int16	1	-32768 to 32768	/Ac/L3/Power	no	W
com.victronenergy.genset	Phase 1 frequency	3209	uint16	100	0 to 655.36	/Ac/L1/Frequency	no	Hz
com.victronenergy.genset	Phase 2 frequency	3210	uint16	100	0 to 655.36	/Ac/L2/Frequency	no	Hz
com.victronenergy.genset	Phase 3 frequency	3211	uint16	100	0 to 655.36	/Ac/L3/Frequency	no	Hz
com.victronenergy.genset	Generator model	3212	uint16	1	0 to 65536	/ProductId	no
com.victronenergy.genset	Status	3213	uint16	1	0 to 65536	/StatusCode	no	0=Standby;1=Startup 1;2=Startup 2;3=Startup 3;4=Startup 4;5=Startup 5;6=Startup 6;7=Startup 7;8=Running;9=Stopping;10=Error
com.victronenergy.genset	Error	3214	uint16	1	0 to 65536	/ErrorCode	no	0=No error;1=AC voltage L1 too low;2=AC frequency L1 too low;3=AC current too low;4=AC power too low;5=Emergency stop;6=Servo current too low;7=Oil pressure too low;8=Engine temperature too low;9=Winding temperature too low;10=Exhaust temperature too low;13=Starter current too low;14=Glow current too low;15=Glow current too low;16=Fuel holding magnet current too low;17=Stop solenoid hold coil current too low;18=Stop solenoid pull coil current too low;19=Optional DC out current too low;20=5V output voltage too low;21=Boost output current too low;22=Panel supply current too high;25=Starter battery voltage too low;26=Startup aborted (rotation too low);28=Rotation too low;29=Power contactor current too low;30=AC voltage L2 too low;31=AC frequency L2 too low;32=AC current L2 too low;33=AC power L2 too low;34=AC voltage L3 too low;35=AC frequency L3 too low;36=AC current L3 too low;37=AC power L3 too low;62=Fuel temperature too low;63=Fuel level too low;65=AC voltage L1 too high;66=AC frequency too high;67=AC current too high;68=AC power too high;70=Servo current too high;71=Oil pressure too high;72=Engine temperature too high;73=Winding temperature too high;74=Exhaust temperature too low;77=Starter current too low;78=Glow current too high;79=Glow current too high;80=Fuel holding magnet current too high;81=Stop solenoid hold coil current too high;82=Stop solenoid pull coil current too high;83=Optional DC out current too high;84=5V output voltage too high;85=Boost output current too high;89=Starter battery voltage too high;90=Startup aborted (rotation too high);92=Rotation too high;93=Power contactor current too high;94=AC voltage L2 too high;95=AC frequency L2 too high;96=AC current L2 too high;97=AC power L2 too high;98=AC voltage L3 too high;99=AC frequency L3 too high;100=AC current L3 too high;101=AC power L3 too high;126=Fuel temperature too high;127=Fuel level too high;130=Lost control unit;131=Lost panel;132=Service needed;133=Lost 3-phase module;134=Lost AGT module;135=Synchronization failure;137=Intake airfilter;139=Lost sync. module;140=Load-balance failed;141=Sync-mode deactivated;142=Engine controller;148=Rotating field wrong;149=Fuel level sensor lost;150=Init failed;151=Watchdog;152=Out: winding;153=Out: exhaust;154=Out: Cyl. head;155=Inverter over temperature;156=Inverter overload;157=Inverter communication lost;158=Inverter sync failed;159=CAN communication lost;160=L1 overload;161=L2 overload;162=L3 overload;163=DC overload;164=DC overvoltage;165=Emergency stop;166=No connection
com.victronenergy.genset	Auto start	3215	uint16	1	0 to 65536	/AutoStart	no	0=Disabled;1=Enabled
com.victronenergy.genset	Engine load	3216	uint16	1	0 to 65536	/Engine/Load	no	%
com.victronenergy.genset	Engine speed	3217	uint16	1	0 to 65536	/Engine/Speed	no	RPM
com.victronenergy.genset	Engine operating hours	3218	uint16	0,01	0 to 6553600	/Engine/OperatingHours	no	s
com.victronenergy.genset	Engine coolant temperature	3219	int16	10	-3276.8 to 3276.8	/Engine/CoolantTemperature	no	Degrees celsius
com.victronenergy.genset	Engine winding temperature	3220	int16	10	-3276.8 to 3276.8	/Engine/WindingTemperature	no	Degrees celsius
com.victronenergy.genset	Engine exhaust temperature	3221	int16	10	-3276.8 to 3276.8	/Engine/ExaustTemperature	no	Degrees celsius
com.victronenergy.genset	Starter voltage	3222	uint16	100	0 to 655.36	/StarterVoltage	no	V DC
com.victronenergy.genset	Start generator	3223	uint16	1	0 to 65536	/Start	yes	0=Stop;1=Start
com.victronenergy.temperature	Product ID	3300	uint16	1	0 to 65536	/ProductId	no
com.victronenergy.temperature	Temperature scale factor	3301	uint16	100	0 to 655.35	/Scale	no
com.victronenergy.temperature	Temperature offset	3302	int16	100	-327.68 to 327.67	/Offset	no
com.victronenergy.temperature	Temperature type	3303	uint16	1	0 to 65536	/TemperatureType	no	0=Battery;1=Fridge;2=Generic
com.victronenergy.temperature	Temperature	3304	int16	100	-327.68 to 327.67	/Temperature	no	Degrees celsius
com.victronenergy.temperature	Temperature status	3305	uint16	1	0 to 65536	/Status	no	0=OK;1=Disconnected;2=Short circuited;3=Reverse Polarity;4=Unknown
com.victronenergy.pulsemeter	Aggregate (measured value)	3400	uint32	1	0 to 4294967295	/Aggregate	no	m3
com.victronenergy.pulsemeter	Count (number of pulses on meter)	3402	uint32	1	0 to 4294967295	/Count	no
com.victronenergy.digitalinput	Count	3420	uint32	1	0 to 4294967295	/Count	no
com.victronenergy.digitalinput	State	3422	uint16	1	0 to 1	/State	no	0=Low;1=High;2=Off;3=On;4=No;5=Yes;6=Open;7=Closed;8=Alarm;9=OK;10=Running;11=Stopped
com.victronenergy.digitalinput	Alarm	3423	uint16	1	0 to 2	/Alarm	no	0=No alarm;2=Alarm
com.victronenergy.digitalinput	Type	3424	uint16	1	0 to 65536	/Type	no	2=Door;3=Bilge pump;4=Bilge alarm;5=Burglar alarm;6=Smoke alarm;7=Fire alarm;8=CO2 alarm
com.victronenergy.generator	Manual Start	3500	uint16	1	0 to 1	/Generator0/ManualStart	yes	0=Stop generator; 1=Start generator
com.victronenergy.generator	Condition that started the generator	3501	uint16	1	0 to 65536	/Generator0/RunningByConditionCode	no	0=Stopped;1=Manual;2=TestRun;3=LossOfComms;4=Soc;5=AcLoad;6=BatteryCurrent;7=BatteryVoltage;8=InverterTemperatur;9=InverterOverload;10=StopOnAc1
com.victronenergy.generator	Runtime in seconds	3502	uint16	1	0 to 65536	/Generator0/Runtime	no	seconds
com.victronenergy.generator	Runtime in seconds	3504	uint32	1	0 to 4294967295	/Generator0/Runtime	no	seconds
com.victronenergy.generator	Generator start/stop state	3506	uint16	1	0 to 65536	/Generator0/State	no	0=Stopped;1=Running;10=Error
com.victronenergy.generator	Generator remote error	3507	uint16	1	0 to 65536	/Generator0/Error	no	0=No Error;1=Remote disabled;2=Remote fault	Only used for FisherPanda gensets
com.victronenergy.generator	Generator not detected at AC input alarm	3508	uint16	1	0 to 65536	/Generator0/Alarms/NoGeneratorAtAcIn	no	0=No alarm;2=Alarm
com.victronenergy.meteo	Solar irradiance	3600	uint16	10	0 to 6553.5	/Irradiance	no	W/m^2
com.victronenergy.meteo	Wind speed	3601	uint16	10	0 to 6553.5	/WindSpeed	no	m/s
com.victronenergy.meteo	Cell temperature of sensor	3602	int16	10	-3276.8 to 3276.7	/CellTemperature	no	Degrees celsius
com.victronenergy.meteo	External temperature	3603	int16	10	-3276.8 to 3276.7	/ExternalTemperature	no	Degrees celsius

## Unit ID mapping
Unit ID	/DeviceInstance	Remark
246	257	CCGX VE.Bus port (ttyO1)
247	256	CCGX VE.Direct 1 port (ttyO0)
245	258	CCGX VE.Direct port 2, Venus GX VE.Direct port 1, Octo GX port 1 (ttyO2)
243	260	Venus GX VE.Direct port 2, Octo GX port 2 (ttyO4)
242	261	Venus GX VE.Bus port (ttyO5)
230	273	EasySolar-II/Multiplus-II GX VE.Direct port (ttyS1)
229	274	EasySolar-II/Multiplus-II GX VE.Direct port (ttyS2)
228	275	EasySolar-II/Multiplus-II GX VE.Bus port (ttyS3)
227	276	Cerbo GX VE.Bus port (ttyS4)
226	279	Cerbo GX VE.Direct port 1 (ttyS7)
224	278	Cerbo GX VE.Direct port 2 (ttyS6)
223	277	Cerbo GX VE.Direct port 3 (ttyS5)
100	0	VE.Can device instance 0 and all registers listed as com.victronenergy.system
1	1	VE.Can device instance 1
2	2	VE.Can device instance 2
3	3	VE.Can device instance 3
4	4	VE.Can device instance 4
5	5	VE.Can device instance 5
6	6	VE.Can device instance 6
7	7	VE.Can device instance 7
8	8	VE.Can device instance 8
9	9	VE.Can device instance 9
10	10	VE.Bus AC-Sensor on input 1
11	11	VE.Bus AC-Sensor on output
12	12	VE.Bus AC-Sensor on input 2
20	20	PV Inverter instance 0
21	21	PV Inverter instance 1
22	22	PV Inverter instance 2
23	23	PV Inverter instance 3
24	24	PV Inverter instance 4
25	25	PV Inverter instance 5
26	26	PV Inverter instance 6
27	27	PV Inverter instance 7
28	28	PV Inverter instance 8
29	29	PV Inverter instance 9
30	30	Carlo Gavazi grid meters instance 0
31	31	Carlo Gavazi grid meters instance 1
32	32	Carlo Gavazi grid meters instance 2
33	33	Carlo Gavazi grid meters instance 3
34	34	Carlo Gavazi grid meters instance 4
40	40	Redflow system totals
41	41	Redflow battery (Modbus-RTU ID 1)
42	42	Redflow battery (Modbus-RTU ID 2)
43	43	Redflow battery (Modbus-RTU ID 3)
44	44	Redflow battery (Modbus-RTU ID 4)
45	45	Redflow battery (Modbus-RTU ID 5)
46	46	Redflow battery (Modbus-RTU ID 6)
239	288	VE.Direct via USB (ttyUSB0)
238	289	VE.Direct via USB, Octo GX VE.Direct 3 (ttyUSB1)
237	290	VE.Direct via USB, Octo GX VE.Direct 4 (ttyUSB2)
236	291	VE.Direct via USB, Octo GX VE.Direct 5 (ttyUSB3)
235	292	VE.Direct via USB, Octo GX VE.Direct 6 (ttyUSB4)
233	293	VE.Direct via USB, Octo GX VE.Direct 7 (ttyUSB5)
232	294	VE.Direct via USB, Octo GX VE.Direct 8 (ttyUSB6)
231	295	VE.Direct via USB, Octo GX VE.Direct 9 (ttyUSB7)
234	296	VE.Direct via USB, Octo GX VE.Direct 10 (ttyUSB8)
225	512	CAN-bus BMS

Note on finding the modbus Unit ID
On the CCGX go to the device list and open the device of interest, then open the Device subsection. This section will have a device instance entry. Use this table to find the unit ID (column A) that matches the device instance (column B). In general the unit ID will be equal to the device instance, except when the device instance exceeds 247. If the device instance is 0 you can use both 0 and 100 as unit ID. Keep in mind that many modbus TCP clients do not support unit ID 0.

## Document versions
Rev 0	Initial version
Rev 1	Fixed numbering error: bmv state of charge and time to go both had id 266. Note that all bmv numbers higher than 266 have now been shifted one up!
Rev 2	The shift of rev 1 has been undone: no shifting. So set time to go to 301, and leave the rest as it was in rev 0
Rev 3	Changed the unitids, because some PLCs do not accept a modbustcp unitd above than 247:
		VE-Bus port was 254, is now 246
		VE.Direct port 1 was 255, is now 247
		VE.Direct port 2 was 253, is now 245
	Added com.victronenergy.charger: Skylla-i. Requires CCGX v1.16 or higher.
Rev 4	Added Hub4 parameters (preliminary!)
	Added device instance 10 to 12
	Changed scaling of all battery parameters that are related to Ah (consumed Ah for example) from 10 to -10
Rev 5	Updated Hub4 registers (vebus)
	Added grid meter (com.victronenergy.grid) including registers to control hub-4 control loop\
	Added gps (com.victronenergt.gps)
	Renamed DC D-Bus paths (eg. /Dc/0/V to /Dc/0/Voltage).
	Changed scaling of solar charger daily yield (address 784)
	Added Unit ID's for PV inverters
Rev 6	Added Hub-4 setpoints for phase 2 and 3.
Rev 7	Added battery state of health
	Added solar charger user yield
	Added unit IDs for Redflow and LG batteries
Rev 8	Added CAN.Bus BMS battery parameters
	Added UnitID 100 (maps to UnitID 0)
	Added system parameters (sum of all PV power, grid power,…)
	Added relays
	Added vebus multi phase alarms
	Added vebus Temperature & Voltage sensor alarms
	Added hub4 BatteryLife state
	Added PV inverter disable flag
Rev 9	Added remarks column in field list
	Added some helpful information on finding the unit ID
	Added VE.Bus BMS paths
Rev 10	Added remark that unit ID is also used for system device
	Added VE.Direct inverters
	Added Fisher Panda generators
	Added tank sensors
	Added ESS grid power setpoint with a smaller scale factor (allows setting power > 32kW)
	Added Lynx Ion BMS.
		Note that in systems with both a Lynx Ion shunt and Lynx Ion bms, there will be 2 battery services now. One of them will have device instance 0, the other 1. In older CCGX firmwares, both could have device instance 0. In that case the modbus TCP user will have to change the unit ID: use unit ID 1 for all battery registers < 1200 instead of ID 0.
Rev 11	Renamed hub-4 to ESS is descriptions and remarks
Rev 12	Added Unit IDs for Venus GX tty ports
	Added temperature sensors
	Added ESS minimum SoC
Rev 13	Added active input source
	Added voltage and current readings to grid servce
	Added support for reading digital inputs
Rev 14	Put the system device on top, and removed references to unit-id 0 from the remarks of the com.victronenergy.system registers.
Rev 15	Add ESS Mode 2 and 3 to the remarks of those registers
	Some other small textual improvements.
Rev 16	Added registers for battery alarms
	Changed battery relay to be writeable (only works with some batteries).
	Added LowCellVoltage alarm for Lynx batteries
	Added VE.Bus temperature
	Added VE.Bus reset
Rev 17	Added registers for generator start/stop
Rev 18	Added register for ESS mode
	Added register for vebus phase rotation warning
	Added register for solar charger’s MPP operation mode
Rev 19	Added register for ESS mode 2 maximum discharge current
	Added register for DVCC maximum system charge current
Rev 20	Added 32-bit energy registers for PV-inverters
Rev 21	Added registers for IMT solar irradiation sensors
Rev 22	Moved 32-bit energy registers added in Rev-20 because they overlapped with the serial number
Rev 23	Added register for GridLost alarm
Rev 24	Added mapping for EasySolar-II/Multiplus-II GX VE.Bus port
Rev 25	Added GPS Altitude
Rev 26	Corrected Dbus path for generator ManualStart
Rev 27	Add mappings for Cerbo GX ports
Rev 28	Added mapping for EasySolar-II/Multiplus-II GX VE.Direct ports
	Added mappings for up to 9 USB-connected VE.Direct devices
	Added Octo-GX mappings
Rev 29	GridLost alarm moved to the vebus service
	Add register for maximum system grid feed in
Rev 30	Added registers for AC-coupled and DC-coupled grid feed-in
	Added register indicating whether Feed-in limiting is active
	Added registers for feeding in overvoltage/excess DC-coupled power and limiting the amount
	Added 32-bit register for generator runtime.
Rev 31	Added additional registers for generator start/stop
Rev 32	Corrected the allowed ranges for many of the registers